## Sheet1
3.1 Cooling Energy Analysis
Cooling Information
Connection Type | Firm |  | Consider all areas under 1 contract
Deal Term | 30 years
Building Construction Start | 2025
Enwave Construction Start | 2024
First Year Occuancy | 2025
Occupancy Ramp Up | 100%
Existing site - contracted
Total - Cooling Analysis | Enwave Returns
Firm Cooling Capacity - Total | 1437.5 | tons | As confirmed by Continual/ KingSett
Expected Peak Cooling Capacity - Total | 1250 | tons
Expected Peak Cooling Capacity w/ Sys. Div. - Total | 1125 | tons
Enwave Returns
Cooling Consumption - Total | 3574406.5013 | Ton-hrs
Cooling FLHs - Total | 2859.5252 | FLH
Save On Energy Incentive - Retrofits Only
Avoided Plant Efficiency | 0.8 | kW/ton | Estimate of future chiller efficiency
Enwave Cooling Electrical Efficiency | 0.28 | kW/ton | From 2022 EPL Report (system efficiency)
Cooling Peak | 1250 | Tons | from 2019 hourly cooling data
Cooling Consumption | 3574406.5013 | Thrs | from 2019 hourly cooling data
Cooling Peak savings | 650 | kW | from 2019 hourly cooling data
Cooling Consumption savings | 3574406.5013 | Thrs | from 2019 hourly cooling data
kWh Before | 2859525.2011 | kWh
kWh After | 1000833.8204 | kWh
kWh savings | 1858691.3807 | kWh
Demand Incentive Rate | 1200 | $/kW | https://saveonenergy.ca/en/News-and-Updates/May-2023-Retrofit-program-update
Consumption Incentive Rate | 0.13 | $/kWh | https://saveonenergy.ca/en/News-and-Updates/May-2023-Retrofit-program-update
Incentive (Demand-Based) $ | 780000 | $
Incentive (Consumption-Based) $ | 241629.8795 | $
Selected Incentive (Greater of the two) $ | 780000 | $